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April 2, 2010
Alliant Energy

2320 Power Plant Drive, 

Lansing, IA  52151
ATTN: Andy Johnson
RE: 
Alliant - Lansing


File # 03-03-001
Please find enclosed one copy of a report resulting from the inspection of your 

facility by  FORMDROPDOWN 
 of our Field Office staff on Mar.

It is hoped that this report will be self-explanatory.  However, should you have any questions, feel free to contact this office.

Sincerely,

ENVIRONMENTAL SERVICES DIVISION
 FORMDROPDOWN 

 FORMDROPDOWN 

Enc.

c:  DNR - Air Quality Bureau - Des Moines

     File – Air/03-03-001
     e-file - 03 AQ Lansing 0303001 Alliant 032310 ins cwo.doc
Page    1  of  
IOWA DEPARTMENT OF NATURAL RESOURCES

ENVIRONMENTAL SERVICES DIVISION

AIR QUALITY COMPLIANCE INSPECTION

FIELD OFFICE # 1                    FACILITY # 03-03-001

Title V – 98-TV-016

 1.  Company Name:  Alliant Energy Corporation, Lansing Power Station
 2.  Company Address: 2320 Power Plant Drive, Lansing, IA  52151
 3.  Plant Address: Same
 4.  Process and/or Product Type:  Electrical Generation
5.  Check Pollutant(s), Air Program Code(s), State Pollutant/Classification(s)

      as a total plant as they correspond with each other:

                                                                                                                                     * Check only if
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VISIT NUMBER 
1
2
INSPECTION CODE

13.  Inspection Code
2

14.  Inspection Date
3/23/10

15.  Time Arrive
10:30 am

16.  Wind Speed & Direction
S @ 5-10

17.  Sky Conditions
Clear

18.  Inspection status
Complete

19.  Time Depart
11:45 am

29.  Persons Contacted:
Andy Johnson  
Phone:
563-538-3110 



30. Inspector's Signature:  _____________________________________
Date: _______________


 FORMDROPDOWN 

31.  Division Approval By:  _____________________________________
Date:  _______________


 FORMDROPDOWN 

* check only the pollutant(s) that this pertains to.
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	BST1
	Generating unit #1

(common stack with #2)  LB1

Gen.unit #2

(common stack with #1)   LB2
	1974
	74-A-097s2
	23.3(2)b&d

23.3(3)a
	EP
	See permit.
	Not operating
	
	
	X
	
	3
	
	
	3/23/10


	BST3
	Gen. unit #3   LB3
SO limit dem. by CEM - 410 lb/hr & 5.0 lb/MMBTU (3-hour ave)
	1973
	73-A-132P-s4
	23.3(2)b&d

23.3(3)a
	EP
	No op when BST1 is
	Not operating
	
	
	X
	
	3
	
	
	3/23/10



	BST4 
	Gen unit #4     NSPS    LB4 maintain record of insp/maint. install CO CEM
	1975
	75-A-014P-S8
	23.1(2)a

NSPS
	BF
	Maintained per mfg.spec.
	Operating
	X
	24 hr/7 day
	X
	17
	3
	
	
	3/23/10



	DC1A

DC1B
	Coal transfer reclaim tunnel  LDC1A&B
	1975
	75-A-190s1
75-A-191s1
	23.3(2)a&d
	BF
	Records on filter maint.
	Not operating
	
	
	X
	
	3
	
	
	3/23/10

	DC2A

DC2B
	Unit #4 coal bunker  LDC2
	1975
	75-A-192-S4
75-A-193
	23.3(2)a&d
	BF
	Records on filter maint.
	Not operating
	
	
	X
	
	3
	
	
	3/23/10


	LD1
	GE Diesel Engine

See permit for record keeping req.
	
	07-A-1333
	23.3(2)a&d

23.3(3)b
	N
	S ≤ .17% by wt.

No operation when T/R on ESP for Boiler 3 taken off line
	Not operating
	
	
	X
	
	3
	
	
	3/23/10


	LD2
	GE Diesel Engine 

See permit for record keeping req.
	
	07-A-1334
	23.3(2)a&d

23.3(3)b
	N
	
	Not operating
	
	
	X
	
	3
	
	
	3/23/10


	EG1
	Emergency lighting diesel generator

LEG1
	
	98-TV-016
	23.3(2)b&d

23.3(2)b
	N
	250 kva
	Not operating
	
	
	
	
	
	
	
	

	ASH1
	Unit #4 Fly ash storage silos

LASH1, LASH2A, LASH2B
	Mod.

1999
	95-A-846-S2
	22.3(1)
	BF
	25% ind. Opac.

Wkly monit.
	Not operating
	
	
	X
	
	3
	
	
	3/23/10


	ASH2
	Ash Silo Unloader  LASH2

And C-Stone Production
	
	98-TV-016
	23.3(2)c

Fugitive Dust
	N
	25 tons/hr
	Not operating
	
	
	
	
	
	
	
	

	ASH3
	Ash Pile  LASH3
	
	98-TV-016
	23.3(2)c

Fugitive Dust
	N
	6.0 Acres of fly ash.
	Not operating
	
	
	
	
	
	
	
	

	CP1

CP2
	CP1 - 7.35 Acre Coal Pile

CP2 - 5.17 Acre Coal Pile
	
	98-TV-016
	23.3(2)c

Fugitive Dust
	N
	Coal pile, open storage
	Not operating
	
	
	
	
	
	
	
	

	CP3

CP4
	CP3 - Coal Unloading

CP4 - Coal Stockpiling
	
	98-TV-016
	23.3(2)c

Fugitive Dust
	N
	1250 tons/hr
	Not operating
	
	
	
	
	
	
	
	

	CP5
	Coal Conveying
	
	98-TV-016
	23.3(2)c

Fugitive Dust
	N
	650 tons/hr
	Not operating
	
	
	
	
	
	
	
	


	Compliance Status
0 - Not Operating/Unknown                5 - On ERP Schedule

1 - Not in Compliance                          6 - Not on ERP Schedule

2 - In Compliance - Test                      9 - Removed

3- In Compliance - Insp.
	Control Equipment Code

BF - Bag Filter                                     MC - Multiclone                          SC - Scrubber                                   WW - Waterwall

EP - Electrostatic Precip.  Cyclone      CR - Cone Roof                          VS - Venturi Scrubber                      DF - Dry Filter

CY - Cyclone                                        FX - Fixed Roof                          PBS - Packed Bed Scrubber             O - Other

A - Afterburner                                      IFR - Internal Floating Roof      PCS - Packed Column Scrubber       N - No Control
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	CP6
	Coal Pile Bulldozing
	
	98-TV-016
	23.3(2)c

Fugitive Dust
	N
	
	Not operating
	
	
	
	
	
	
	
	

	SS1
	Sorbent Silo
	2008
	08-A-055
	23.3.3(2)d
	Cart. Filter
	Maintain according to mfg.
	Under construction
	
	
	
	
	
	
	
	

	LASH4A
	Ash Silo 4 (Silo Filling Exhaust)
	2009
	09-A-190S1
	23.3.3(2)a&d
	BF
	None
	Under construction
	
	
	
	
	
	
	
	

	ACS1
	Activated Carbon Silo
	2009
	09-A-191
	23.3.3(2)a&d
	BF
	None
	Under construction
	
	
	
	
	
	
	
	

	LASH4B
	Ash Silo 4 (Truck Filling Exhaust)
	2009
	09-A-334
	23.3.3(2)a&d
	BF
	None
	Under construction
	
	
	
	
	
	
	
	

	LASH 4C
	Ash Silo 4 (Silo Vent)
	2009
	09-A-335
	23.3.3(2)a&d
	BF
	None
	Under construction
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	


	Compliance Status
0 - Not Operating/Unknown                5 - On ERP Schedule

1 - Not in Compliance                          6 - Not on ERP Schedule

2 - In Compliance - Test                      9 - Removed

3- In Compliance - Insp.
	Control Equipment Code

BF - Bag Filter                                     MC - Multiclone                          SC - Scrubber                                   WW - Waterwall

EP - Electrostatic Precip.  Cyclone      CR - Cone Roof                          VS - Venturi Scrubber                      DF - Dry Filter

CY - Cyclone                                        FX - Fixed Roof                          PBS - Packed Bed Scrubber             O - Other

A - Afterburner                                      IFR - Internal Floating Roof      PCS - Packed Column Scrubber       N - No Control
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IOWA DEPARTMENT OF NATURAL RESOURCES

ENVIRONMENTAL SERVICES DIVISION

AIR QUALITY INDIVIDUAL SOURCE EVALUATION

	1.  Source ID

                         BST1
	Source Description & Location

      Generating unit #1
	2.  Date of Evaluation


	3.  Baseline Operation Parameters (from stack test, order, or permit)


	4.  Observed This Date


	Production/Process Rate
	120,000 lbs. steam / hour
	

	  Opacity (v.e. or CEM)
	40 % per T. 5 permit
	

	  SO2 Emissions (CEM)
	5 lb/MMBtu per T. 5 permit
	

	  Particulate Matter
	0.6 lb/MMBtu Per T.5 w/boiler 2 only
	Determined at stack test

	  Particulate Matter
	0.37 lb/MMBtu w/boilers 1,2 and 3 op

0.6 lb/MMBtu w/boilers 1 and 2 op.
	Determined at stack test


	Fuel Type / Boilers
	coal
	
	
	

	Fuel Source (if coal)
	Eastern
	
	
	

	% Ash
	
	
	
	

	% Sulfur
	
	
	
	

	BTU
	
	
	
	

	% Use
	100 %
	
	
	


	Control Equipment Description/Operation

Parameters


	Electrostatic precipitator

common stack with unit # 2
	


	5.  Continuous Monitoring Reference Value   (Quarterly Report)
	Opacity
	SO2
	NOX
	O2/CO2

	Zero Value
	
	
	
	

	SPAN Value
	
	
	
	


	6.  Continuous Monitoring  Value Observed This  Date
	Opacity
	SO2
	NOX
	O2/CO2

	Zero Value
	
	
	
	

	SPAN Value
	
	
	
	


	7.  Recordkeeping
	[ ] Adequate     [ ] Inadequate (comment below)


	8.  Compliance Status/Comments




       INSPECTOR INITIAL                                                                                                                                                                    542-3025  (rev 10/94)

	Field Office 1,  909 West Main Suite 4, Manchester, IA  52057

563/927-2640
FAX 563/927-2075



