	[image: image1.png]



	Written Report for Hazardous Conditions

The Iowa Department of Natural Resources 
Requires a written report of any Hazardous Condition.
(VERBAL REPORT REQUIRED WITHIN 6 HOURS)


Written Report. The written report of a hazardous condition shall be submitted to the department within 30 days and contain the following information   (Please complete as much as possible):

	DNR Spill Number for hazardous condition:
	040517-TMN-1550


Location of hazardous condition:

	Physical Address
	7215 Navajo Street
	city
	Council Bluffs

	Legal Address
	Lat/Long or Twn/Rng        
	zip
	51501

	Other description
	     


Time and Date of onset or discovery of hazardous condition:
	Time
	15:00   FORMCHECKBOX 
 AM   FORMCHECKBOX 
 PM
	Date
	04/05/17


Time and Date of verbal report to the department of the hazardous condition:

	Time
	15:50   FORMCHECKBOX 
 AM   FORMCHECKBOX 
 PM
	Date
	04/05/17


The Hazardous Condition:
	Name of material/substance(s)
	Manufacturer
	Volume

	Fuel Oil
	     
	est. 3606 gallon(s)

	     
	     
	     

	     
	     
	     

	     
	     
	     


If more space is needed add additional pages.  Attach a Material Safety Data Sheet (MSDS) if possible.

The medium in which the hazardous condition occurred/existed (Check all that apply):

 FORMCHECKBOX 
 Ground Water                FORMCHECKBOX 
 Surface Water                     FORMCHECKBOX 
 Land                    FORMCHECKBOX 
 Air

Weather Conditions during the time of the hazardous condition onset or discovery:

	Temperature
	Wind Direction
	Wind Speed
	Humidity
	Precipitation

	45
	Calm
	     
	     
	Cloudy


Contact Information:

	
	Name
	Company
	Mailing Address
	Telephone

	Person Reporting 

(if known)
	Danielle Leslie
	MidAmerican Energy Company
	106 East 2nd Street Davenport, IA 52801
	 563-333-8175

	Party Responsible 
	     
	     
	     
	     

	Site Contact
	Brian Kost
	MidAmerican Energy Company
	7215 Navajo Street Council Bluffs,IA 50501
	712-366-7196


Cause of the Incident:  Write a narrative of the events leading to the incident

	On April 5, 2017, a pressure loss was observed during integrity testing on the on the Unit 3 return underground piping to the aboveground fuel oil storage tanks  at the Walter Scott Jr. Energy Center.  A leak in the piping has not been visually confirmed; however, fuel oil has been observed the Unit 3 chemical waste sump intermittently since January 19, 2017, and recovered for proper disposal. Initially the leak was thought to be from an above ground equipment source and entering the drain line leading to the chemical waste sump.  Integrity testing of the underground fuel oil piping was performed on January 25, 2017 and February 14, 2017, and tests did not indicate any deficiencies or indications of a release.  On February 27, 2017, a camera inspection was performed on the chemical waste sump drain line as part of continued investigation activities to determine the source of fuel oil and a breach was identified in the drain line.  The Iowa Department of Natural Resources (IDNR) was notified of the drain line breach and fuel oil discovery on March 1, 2017, and that based on information collected, it appeared the fuel oil in the chemical waste sump was related to the 2013 or 2015 underground fuel oil pipe releases. 

After the failed integrity test on April 5, 2017, IDNR was timely notified and the return underground piping was isolated and construction was initiated for temporary aboveground piping was  while continuing recovery of fuel oil from the chemical waste sump.  On April 6, 2017, environmental services and facility staff participated in a conference call with IDNR to discuss the Unit 3 underground return fuel oil piping release. The department conducted a site visit April 7, 2017, to observe recovery efforts. On April 8, 2017, the temporary aboveground pipe installation was completed, successfully pressure-tested and placed into operation to allow permanent isolation of the leaking section of underground piping. The 3,606 gallons represents the amount recovered since January 19, 2017; however, the total amount released is unknown.  Further investigation activities to identify the leak location remains ongoing and is anticipated to be completed the week of  May 8, 2017.



Initial Actions Taken:  Write a narrative of the initial actions and instructions taken or required.

	No material reached a drain or waterway in the area where the material was released. Facility will work with contaminated sites to mediate as appropriate. 


Written reports should include the DNR spill number and be addressed to the duty officer responding to the spill.  Reports can be sent via mail, fax, or electronic mail.

	Mail
	Fax
	Email

	IDNR Emergency Response

7900 Hickman Rd Ste 200
Windsor Heights, IA 50324-4432
	515/281-7229
	Emergency_Response@dnr.iowa.gov


Thank You 

02/2014 cmz

DNR Form 542-0029


