	[image: image1.jpg]Fields of Opportunities S TAT E O F | O WA

CHESTER J. CULVER, GOVERNOR DEPARTMENT OF NATURAL RESOURCES
PATTY JUDGE, LT. GOVERNOR RICHARD A. LEOPOLD, DIRECTOR







Evansdale Notice of Violation

August 5, 2010

Page 4

August 5, 2010

City of Evansdale

123 N. Evans Road

Evansdale, IA  50707

ATTENTION:  Mayor and City Council
RE:  Notice of Violation: 567 IAC 63.6(3) Notification of unanticipated bypass
On August 2, 2010, Sue Miller of this offfice met with Mayor Chad Deutsch, WW operator Phillip Stocks, and members of the city staff to discuss wastewater bypasses that had occurred as a result of heavy rains that fell on the area during July 2010.  The City had reported by telephone on July 7, 2010 at 8:20 AM that wastewater would be bypassing treatment at the Arbutus and LaFayette lift stations.  Information submitted to this office on August 2 indicates that bypasses occurred at eight additional locations during that wet weather event.  These additional bypasses were not reported to the department.   It also came to light that during a subsequent rain event on or about July 14, 2010, several other bypasses occurred including one at a manhole located at the intersection of Miner St. and LaFayette that continued until 12:00 AM on August 3.
This department’s reporting requirements require that these types of events must be reported within 12 hours of discovery or occurrence.  

As a reminder, to be in compliance with the city’s MS4 storm water NPDES permit, every effort should be made to prevent pollutants from entering the storm water collection system.  Part of the storm water collection system includes Meyers Lake, which is the City’s storm water detention pond, but is also a recreational water of the State.
By August 15, 2010, the City must submit a full accounting of all wastewater bypasses that occurred during the month of July 2010 and up through August 3, 2010.  The City must also supply information on all wastewater bypasses that occurred from the City’s system in the past 5 years.  The information should include the location of the bypass, the estimated volume of wastewater discharged, the duration of the discharge and the affected water body.  By September 15, 2010, you must submit a plan the will address the issue of proper reporting of bypass events.  It is highly recommended that this plan include training for city staff that are involved in responding to bypass events.

By December 1, 2010, the City must submit a plan for addressing the excess inflow and infiltration into the City’s sanitary sewer system during wet weather events. As we discussed at our meeting, the City has begun a program of inspecting homes for illegal connections to the sanitary sewer including sump pumps, roof and footing drains, exterior yard, driveway and walkway drains.   The plan must also include a schedule for inspection and repair of sewers and manholes.  

If you have any questions please feet free to contact me at this office.

Sincerely,

ENVIRONMENTAL SERVICES DIVISION

Mike Wade

Environmental Specialist Senior
c:
File – WW/Evansdale

Efile – 07 ww Evansdale nltr 080510 sjm

IDNR 5th Floor Records NPDES #0723001
63.6(3) Notification of unanticipated bypass or upset and public notices. 
In the event that a bypass or upset occurs without prior notice having been provided pursuant to 63.6(2) or as a result of mechanical failure or acts beyond the control of the owner or operator, the owner or operator of the treatment facility or collection system shall notify the department by telephone as soon as possible but not later than 12 hours after the onset or discovery.
a. Notification shall be made by contacting the appropriate field office during normal business hours (8 a.m. to 4:30 p.m.) or by calling the department at (515)281-8694 after normal business hours.
b. Notification shall include information on as many items listed in subparagraphs 63.6(3)“d”(1) through (6) as available information will allow.
c. When the department has been notified of an unanticipated bypass, the department shall determine if a public notice is necessary. If the department determines that public notification is necessary, the owner or operator of the treatment facility or the collection system shall prepare a publicnotice.
d. Bypasses shall be reported with the monthly operation report, as a separate attachment, that includes:

(1) The reason for the bypass, including the amount and duration of any rainfall event that may have contributed to the bypass;

(2) The date and time of onset or discovery of the bypass;

(3) The duration of the bypass;

(4) An estimate of the amount of untreated or partially treated sewage or wastewater that was discharged;

(5) The location of the bypass; and

(6) The name of any body of surface water that was affected by the bypass.
63.6(4) Monitoring, disinfection, and cleanup. 
The owner or operator of the treatment facility or collection system shall perform any additional monitoring, sampling, or analysis of the bypass or upset requested by the regional field office of the department and shall comply with the instructions of the department intended to minimize the effect of a bypass or upset on the receiving water of the state. The following requirements for disinfection and cleanup apply to all bypasses:

a. The department may require temporary disinfection depending on the volume and duration of the bypass, the classification of the stream affected by the bypass, and the time of year during which the bypass occurs; and

b. The department may require cleanup of any debris and waste materials deposited in the area affected by the bypass. In conjunction with the cleanup, the department may require lime application to the ground surface or disinfection of the area with chlorine solution.

63.6(5) Reporting of subsequent findings and additional information requested by the

department. 
All subsequent findings and laboratory results concerning a bypass shall be submitted in writing to the appropriate regional field office of the department as soon as they become available. Any additional information requested by the department concerning the steps taken to minimize the effects of a bypass shall be submitted within 30 days of the request.

	Field Office 1, 909 West Main Suite 4, Manchester, IA  52057

563/927-2640
FAX 563/927-2075



[image: image1.jpg]