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	Written Report for Hazardous Conditions

The Iowa Department of Natural Resources
Requires a written report of any Hazardous Condition.

(VERBAL REPORT REQUIRED WITHIN 6 HOURS)


Written Report. The written report of a hazardous condition shall be submitted to the department within 30 days and contain the following information (Please complete as much as possible):

	DNR Spill Number for hazardous condition:
	NA
	

	Location of hazardous condition:

	Physical Address
	5450 Locust Rd. SW
	City
	Cedar Rapids

	Legal Address Lat/Long or Twn/Rng
	T82N R7W S8
	Zip
	 S852404

	Other description
	     

	Time and Date of onset or discovery of hazardous condition:

	Time
	7:03 
	 FORMCHECKBOX 
 AM  FORMCHECKBOX 
 PM
	Date
	6/29/2020
	

	Time and Date of verbal report to the department of the hazardous condition:

	Time
	9:55 
	 FORMCHECKBOX 
 AM  FORMCHECKBOX 
 PM
	Date
	6/29/2020
	

	Hazardous Condition:

	Name of material/substance(s)
	Manufacturer
	Volume

	Cooling Tower Water
	     
	20,250 gallons (est.)

	     
	     
	     

	     
	     
	     

	     
	     
	     

	If more space is needed add additional pages. Attach a Material Safety Data Sheet (MSDS) if possible.

	The medium in which the hazardous condition occurred/existed (Check all that apply):

	
	 FORMCHECKBOX 
 Ground Water
	 FORMCHECKBOX 
 Surface Water
	 FORMCHECKBOX 
 Land
	 FORMCHECKBOX 
 Air

	Weather Conditions during the time of the hazardous condition onset or discovery:

	Temperature
	Wind Direction
	Wind Speed
	Humidity
	Precipitation

	75 F
	SW
	1-5
	high
	None

	Contact Information:

	
	Name
	Company
	Mailing Address
	Telephone

	Person Reporting 

(if known)
	Rich Stephens
	ADM 
	1350 Waconia Ave. SW
	319-310-0084

	Party Responsible 
	Brian Mullins
	ADM
	1350 Waconia Ave. SW
	319-398-0721

	Site Contact
	Rich Stephens
	ADM
	1350 Waconia Ave. SW
	319-398-0735


Cause of the Incident: Write a narrative of the events leading to the incident

	Cooling tower return line split under the concrete floor below turbine 1. Water geysered up through cracks and ran out the overhead door. Post incident investigation found corrosion allowed for an 8 inch hole to split open on the 42 inch pipe just below floor level. 


Initial Actions Taken: Write a narrative of the initial actions and instructions taken or required.

	De-chlorination of the cooling tower water.  Shutdown of turbine 1. Isolation of the north Cogen cooling tower. Two water transfer pumps were setup to reclaim water to the sanitary sewer system. Good flow on the un-named tributary of Prairie Creek at the time of event. No negative consequences observed on the nearby creek or on Prairie Creek. 


Written reports should include the DNR spill number and be addressed to the duty officer responding to the spill. Reports can be sent via mail, fax, or electronic mail.

	Mail
	Fax
	Email

	DNR Emergency Response

502 E 9th St

Des Moines IA 50319
	515-281-7229
	Emergency_Response@dnr.iowa.gov


Thank You
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