Page    1  of  3
IOWA DEPARTMENT OF NATURAL RESOURCES

ENVIRONMENTAL SERVICES DIVISION

AIR QUALITY COMPLIANCE INSPECTION

FIELD OFFICE # 1                    FACILITY # 31-01-035

                                                             Title V Permit   #01-TV-022R1

 1.  Company Name:  Dubuque Water Pollution Control Plant

 2.  Company Address: 795 Julien Dubuque Drive, Dubuque, IA 52003

 3.  Plant Address: Same

 4.  Process and/or Product Type:  Wastewater Treatment

5.  Check Pollutant(s), Air Program Code(s), State Pollutant/Classification(s)

      as a total plant as they correspond with each other:

                                                                                                                                     * Check only if

                         Pollutant(s)          SIP   NSPS   PSD   NESHAP        
A   SM   B   C   ND          in violation
VOC
(__                
(_
__
__
__
__
__
(_
__
__
___

NOx
(__                
(_
__
__
__
(_
__
__
__
__
___

SOx
(__                
(_
__
__
__
__
__
(_
__
__
___

CO
(__                
(_
__
__
__
__
__
(_
__
__
___

PM10
(__                
(_
__
__
__
__
__
(_
__
__
___

PT
(__                
__
(
__
(_
__
__
(_
__
__
___

OTHER(S)
Hg, Be,Pb THAP __
(
__
(_
__
__
(_
__
__
___

VISIT NUMBER                                                          3                                               INSPECTION CODE

13.  Inspection Code
_2______________                             1.  Complaint

14.  Inspection Date
_16 December 2009                             2.  Routine Insp.

15.  Time Arrive
_9:15 AM________                             3.  Stack Test Obs.

16.  Wind Speed & Direction
_~5 mph Southeast_                            4.  Other - Explain

17.  Sky Conditions
_Clear___________

18.  Inspection status
_Complete________

19.  Time Depart
_10:50 AM________

29.  Persons Contacted:     Johnathan Brown and Bill Junjk       
Phone: 563/589-4176                                     

_______________________________________
Phone:  _____________

30.  Inspector's Signature:  __________________________________________  Date: ____________________

31.  Division Approval By:  _________________________________________ Date:  _____________________

* check only the pollutant(s) that this pertains to.

C: efile 31 AQ Dubuque 3101035 Dubuque Water Pollution Control Plant 121609 ins rpm

10/94                                                                                                                                                                                                                542-1513

IOWA DEPARTMENT OF NATURAL RESOURCES, ENVIRONMENTAL SERVICES DIVISION, AIR QUALITY COMPLIANCE INSPECTION

Company Name: Dubuque Water Pollution Control Plant
 Facility: 31-01-35
 Page   2
of   3
	ID

#

   6
	Source Description & Location

                                                                   7
	I

N

S

T

A  D

L   A

L   T

A   E

T

I

O

N          8
	P    N

E   U

R   M

M  B

I    E

T   R

         9
	Applicable

Regulations

                      10
	Cntl

Code

    11
	Maximum

Capacity or

Operating

Limits

                12
	Actual Operating

Condition (Process

Input Rate)

                        20
	C

N

T

L

EQP

       21
	O  S

P  C

     H

     E

     D

    22
	R K

E E

C E

O P

R  I

D N

    G

   23
	O

P

A

C

I

T

Y

24
	C  S

O  T

M A

P  T

L  U

Y  S

   25
	C

O

M

M

E

N

T

S

26
	I

N  I

S  N

P  I

E  T

C  I

T  A

O  L

R

   27 
	 D

 A

 T

 E

    28

	EP 1
	North Sewage Sludge Incinerator   
	1979
	79-A-014s3
	567IAC Ch20-31 40CFR 51, 52, 60, 61
	VS PBS
	Max Temp 1675(F
	1429(F sludge/fuel oil   (P=27.9”
	OP
	24 Hr/Dy
	(
	0
	1
	(
	
	12/16/09


	EP 2
	South Sewage Sludge Incinerator 
	1979
	01-A-881
	567IAC Ch20-31 40CFR 51, 52, 60, 61
	VS PBS
	Max Temp 1675(F
	Not Operating
	
	
	(
	
	1
	(
	
	12/16/09



	EP 8
	Ash Handling
	
	01-TV-022
	567IAC Ch20-31
	N
	None
	Operating 700 lbs/hr  No outside exhaust
	N/A
	24 Hr/Dy
	N/A
	N/A
	3
	
	
	12/16/09



	EP 9
	Sewage Treatment (Entire Plant)
	
	01-TV-022
	567IAC Ch20-31
	N
	None
	Operating
	N/A
	24 Hr/Dy
	N/A
	N/A
	3
	
	
	12/16/09



	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	INSIGNIFICANT EQUIPMENT
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	P-5
	Individual Space Heaters (34)
	
	01-TV-022
	
	
	
	Operating
	N/A
	As Need
	N/A
	N/A
	3
	
	
	12/16/09



	P-6
	Gasoline Tank
	
	01-TV-022
	
	
	
	Operating
	N/A
	As Need
	N/A
	N/A
	3
	
	
	12/16/09



	P-7
	Diesel Fuel Tank
	
	01-TV-022
	
	
	
	Operating
	N/A
	As Need
	N/A
	N/A
	3
	
	
	12/16/09



	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	
	
	
	


	Compliance Status
0 -Not Operating/Unknown                 5 - On ERP Schedule

1 - Not in Compliance                          6 - Not on ERP Schedule

2 - In Compliance - Test                      9 -Removed

3 - In Compliance - Insp.
	Control Equipment Code

BF - Bag Filter                                     MC - Multiclone                          SC - Scrubber                                   WW - Waterwall

EP - Electrostatic Precip.                     CR - Cone Roof                          VS - Venturi Scrubber                      DF - Dry Filter

CY - Cyclone                                        FX - Fixed Roof                          PBS - Packed Bed Scrubber             O - Other

A - Afterburner                                      IFR - Internal Floating Roof      PCS - Packed Column Scrubber       N - No Control


                                                                                                                                                                                                                                                                                        542-3025  (rev 10/94)

IOWA DEPARTMENT OF NATURAL RESOURCES

ENVIRONMENTAL PROTECTION DIVISION

AIR QUALITY INDIVIDUAL SOURCE EVALUATION

	1.  Source ID   EP 1 and EP 2

	Source Description & Location  North Sewage Sludge Incinerator and South Sewage Sludge Incinerator
	2.  Date of Evaluation                         16 December 2009     


	3.  Baseline Operation Parameters (from stack test, order, or permit)


	4.  Observed This Date


	Production/Process Rate
	
	

	  Opacity (v.e. or CEM)
	
	

	  SO2 Emissions (CEM)
	
	

	  NOX Emissions (CEM)
	
	

	  O2/CO2 (CEM)
	
	


	Fuel Type / Boilers
	
	
	
	

	Fuel Source (if coal)
	
	
	
	

	% Ash
	
	
	
	

	% Sulfur
	
	
	
	

	BTU
	
	
	
	

	% Use
	
	
	
	


	Control Equipment Description/Operation

Parameters


	
	


	5.  Continuous Monitoring Reference Value   (Quarterly Report)
	Opacity
	SO2
	NOX
	O2/CO2

	Zero Value
	
	
	
	

	SPAN Value
	
	
	
	


	6.  Continuous Monitoring  Value Observed This  Date
	Opacity
	SO2
	NOX
	O2/CO2

	Zero Value
	
	
	
	

	SPAN Value
	
	
	
	


	7.  Recordkeeping
	[ ] Adequate     [ ] Inadequate (comment below)


	8.  Compliance Status/Comments

Continuous Emissions Monitoring, page 13, Title V Permit 01-TV-022R1 requires annual calibration of control monitoring equipment monitoring pressure drop (wet scrubber device).  Johnathan Brown, Dubuque Water Pollution Control Plant stated that this requirement has not been met.  This is a violation of Title V Permit 01-TV-022R1.  The facility is directed to perform the required calibration within 60 days of receipt of this report.    
Beginning on page 14 and repeated on additional pages of 01-TV-022R1 is an apparent typographical error.  The permit states, “Therefore the scrubber pressure drop shall not be over 14.14 inches of water.”  Dubuque water control staff believes this should read, “shall be over 14.14 inches of water.”  It is recommended that DWPCP staff contact Julie Ingoli, Iowa DNR Environmental Engineer, ph. 515-242-5100 for guidance.   



       INSPECTOR INITIAL                                                                                                                                                                    542-3025  (rev 10/94)
