	



IOWA DNR UST INSPECTION SUMMARY FORM
Inspection Type:   FORMDROPDOWN 

	Facility Name: Cargill Inc.
	Owner Name: Cargill, Inc. ATTN: Steven Phillips

	Location Address: 1710 16th ST SE
	Mailing Address: PO Box 1467

	City: Cedar Rapids
	City, State, Zip: Cedar Rapids, IA 52401-1467

	Phone: 319/399-2160
	Phone: Same as Site or 319/399-2128

	Operator Name: Steven Phillips
	Mailing Address for Compliance Tags:

	Phone: Same as Above
	Name: 

	Fax: 
	Address:      

	E-mail: steven_phillips@cargill.com
	City, State, Zip:      

	Date of this audit: 03/03/10
	Date of Previous Inspection:

	Date of Compliance Inspection:11/11/09

	Compliance Inspector Name:  Stephen Cox

	Registration No.
	Compliance Inspector Co.
	All applicable tanks registered?
	Current UST tag attached to fill pipe and visible to delivery driver?

	198600807
	Rounds
	 FORMCHECKBOX 
  Yes   FORMCHECKBOX 
  No
	 FORMCHECKBOX 
 Yes   FORMCHECKBOX 
  No

	LUST No. None
	LUST Status:  NA


	Compliance Items
	Tank #  FORMDROPDOWN 

24344
	
	
	

	Tanks registered
	 FORMDROPDOWN 

	
	
	

	Tank tags attached to fill ports
	 FORMDROPDOWN 

	
	
	

	Release Detection (Tank only)
	 FORMDROPDOWN 

	
	
	

	Release Detection (Piping only)
	 FORMDROPDOWN 

	
	
	

	Release Detection Record Keeping *
	 FORMDROPDOWN 

	
	
	

	Spill Device (Tank only)
	 FORMDROPDOWN 

	
	
	

	Overfill Device (Tank only)
	 FORMDROPDOWN 

	
	
	

	Corrosion Protection (Tank only)
	 FORMDROPDOWN 

	
	
	

	Corrosion Protection (Piping only)
	 FORMDROPDOWN 

	
	
	

	Corrosion Protection Record Keeping
	 FORMDROPDOWN 

	
	
	

	Sumps/Secondary Containment
	 FORMDROPDOWN 

	
	
	

	General Record Keeping (installation, repair, closure, availability, etc.)
	 FORMDROPDOWN 

	
	
	

	

	Financial Responsibility 
	 FORMDROPDOWN 

	Insurance Provider:  FORMDROPDOWN 

Mechanism:  FORMDROPDOWN 

	Expiration Date:

08/26/10


I audited this facility 03/03/10   in comparison to Stephen Cox’s 11/11/09 compliance inspection and in reference with the UST requirements of 567—Chapter 135.  The following items need correction:  Copies of sited regulations are enclosed.

1. Tank 24344 did not have the annual tag attached.  In accordance with 567 IAC 135.3(5)c “the owner or operator shall affix the tag to the fill pipe of the underground storage tank where it will be readily visible”.  Delivery drivers are prohibited from dispensing a regulated substance into a tank without tags attached.  Acquire an annual tag and attach the tag where it is readily visible to delivery staff.  The permanent (purple) tag should also be relocated to the fill area.
2. Observation of the overfill device was not possible during the audit inspection.  The tank is filled by use of an above ground coaxial hose leading to a fixed above ground pipe draining to the UST.  Reportedly, there is an automated overfill device present within the drop tube which prohibits overfills.  Note: the above ground portion of the tank system is located within a large secondary containment structure isolated by a perimeter fence.
3. 567 IAC 135.4(2)b(1) requires testing of Cathodic Protection (CP) systems every three years.  Tank 24344 is protected from corrosion by use of galvanic CP.  CP test records were not available during the audit inspection.  Discussion with Steven Phillips and review of the UST database memo field indicates the facility’s certified CP tester has been unable to obtain a passing test.  Paul Nelson, DNR Central Office, has been corresponding with Steven regarding this matter.  Submit a passing CP test to the DNR Central Office when available and have a CP test conducted every three years thereafter.  Maintain results of the previous two CP tests onsite.
There may be another inspection to ensure the above issues have been resolved.  Your prompt correction of these violations will be considered in any decision to take enforcement action.
Comments:  

	INSPECTOR:
Brian Jergenson
	DATE

03/09/10

	REVIEWER:

 FORMDROPDOWN 

	DATE




March 9, 2010






Cargill, INC
ATTN: Steven Phillips

PO Box 1467

Cedar Rapids, IA 52401-1467
SUBJECT: 
Underground Petroleum Storage Tank System Inspection


Cargill Incorporated at 1710 16th Street SE in Cedar Rapids, Iowa.

UST Registration # 198600807
Dear Mr. Phillips:

Enclosed is the summary report for the inspection completed by  FORMDROPDOWN 
 of the Field Office 1 staff at your facility in Cedar Rapids, Iowa.  

You are reminded that the regulations referenced in this report also apply to underground petroleum storage tank facilities you may have at other locations in Iowa.

You may contact  FORMDROPDOWN 
 at 563/927-2640 or this office with any questions or comments.  Thank you for your assistance during this inspection.

Sincerely,

Tom McCarthy
Environmental Specialist Sr. 
Field Office # 1

563-927-2640

cc:
Paul Nelson, IDNR UST Program (w/encl.)



Stephen Cox, Rounds & Associates, PO Box 7628, Urbandale, IA 50323
Efile name: 57 UST Cedar Rapids Cargill ins 030310 bdj






[image: image1.jpg]Fields of Opportunities S TAT E O F | O WA

CHESTER J. CULVER, GOVERNOR DEPARTMENT OF NATURAL RESOURCES
PATTY JUDGE, LT. GOVERNOR RICHARD A. LEOPOLD, DIRECTOR




