Documentation Report

Site Location:  Sivyer Steel Bettendorf, Iowa
Date: 4/22/21

2:49 PM

Received an email from Brian Lee IDNR inspector; Brian informed that he received a complaint of illicit discharge entering a storm drain at Sivyer Steel on 33rd St. 

3:09 PM

The City ESC Tech (Rob DePover) responded to Brian informing that he would look in to it.

Date: 4/22/21

10:50 AM
A call was made to Sivyer Steel asking to speak with someone about the issue. A message was left with Schuyler Bowman Maintenance Manager (563) 355-1811 informing him of the issue and requesting a meeting on site.

10:55 AM

Stopped by the site for a compliant inspection a follow up call was made to Mr. Bowman who agreed to meet on site. Clear unscented water is evident near and inside the catch basin at the end of 33rd St. Mr. Bowman informed that it came from the water recirculation tank just North of the catch basin. The tank is used for recirculated water from a quench tank located inside the Foundry for cooling purposes. Mr. Bowman informed that one of the three recirculating pumps was leaking a few days ago causing the quench tank water to spill over into the secondary confinement tank. A removable barricade (sand bags) on the Southwest corner of the secondary confinement tank was not in place during the time of the leak allowing water to escape. Mr. Bowman informed that the pump has been repaired and weep holes will be drilled on the platform for water to drain into the storage tank if any pumps leak in the future. It was also mentioned that the secondary confinement tank will be fitted with a permanent cement wall on the SW corner to prevent leaking. It is unknown how much water entered the catch basin.
The catch basin leads to a settling basin on site that leads to the Government interceptor which drains to the Mississippi River (see documents and pictures in file)
