Kraft Heinz Mason City - Facility No. 017-01-056

Retification of Deficiencies: EP-7 Wastewater Plant Maintenance Records

Records for the Plant's Environmental Control Facility ("ECF") are maintained in the office of the Plant Utilities Coordinator. ECF contains the plant's wastewater treatment system as well as an air scrubber. The Utilities Support Team at the plant has a weekly area maintenance preventative maintenance procedure ("PM") that includes maintenance to the wastewater treatment system as well as periodic maintenance to the air scrubber. The Iowa Dept. of Natural Resources ("IDNR") representative asked for maintenance activities pertaining to the air scrubber. There are maintenance items on two of the weekly PMs pertaining to specifically to the that equipment. During the inspection the Plant noted that there was not a PM procedure solely dedicated to that piece of equipment. The Plant Utilities Maintenance Planner has now created two PM procedures for the air scrubber per the manufacturer's maintenance interval plans. One SAP PM procedure titled "Odor Control PM" will be executed on a four month interval as time based routine maintenance for the air scrubber. The other PM procedure titled "Annual Odor Control PM" is for a larger maintenance routine as well as annual cleaning of the system. The annual cleaning of the system has always been done at the facility but has not been a documented PM procedure. Both PMs will be executed starting in 2024. The following pages have copies of the maintenance that was completed in 2022 and 2023.