## Sheet1
Reference Number | Audit Item | Comment | Rating | Root Cause | Corrective Action | Targeted Implement Date | Responsible Party | Reviewed Date | Responsible Party | Date Completed | Comment
SIGNIFICANT DEFICIENCIES
2E. | RPZs are not on processing building and the production break room | RPZs should be installed on processing building and production break room prior to domestic use. | Significant Deficiencies | During review of cross connections production break room and processing had not been previously installed with the proper backflow prevention when the areas were built | RPZs will be installed at the proper locations in the processing and production areas by mort's water company. Currently these items are on order and will be installed immediately. | 3/20/2015 | Nick Wilson |  |  | 2015-02-27 | Mort's installed a backflow prevention.
6.01.07 | Does the policy include how to handle loose birds in the layer house? | Three to four loose birds observed in barn 6 (new enrich able type). Employee giving tour stated policy is they wait a week to round up the loose birds. This was not in compliance with internal Loose Hen Policy. This discrepancy should be a documented retraining opportunity with barn employees on this policy. | OBS | Production staffing problems. | Re-Training of the production staff on loose hen replacement policy. | 2014-10-15 | Mark/Myah
2F | Free and total chlorine residuals are not being taken at the source entry point, in the distribution system, nor when the bacterial sampling is being taken. | The chlorine residuals shall be recorded Daily | Significant Deficiencies | Chlorine pumps and test kits were currently none operational and had not been functioning for some time. | Chlorine pumps have been ordered and chlorine tests have been ordered. | 2015-03-19 | Nick Wilson |  |  | 2015-04-20 | oldson plumbing is coming Monday to install. Morts has not came out to install yet so I have contacted oldsen plumbing. 4/20/15
8A. | Chapter 455B section 223 of Iowa code of Iowa requires a certified operator for water treatment plants . | Plant did not have a properly certified operator. | Significant Deficiencies | Current operator was not an on site operator. | Sparboe Goodell will send three operators to the April 8th water operator training and certification class. | 2015-04-10 | Nick Wilson |  |  |  | Have taken work shop class, will need to get time scheduled for state test. With A.I. in iowa we have been busy with high bio-security measures and hadnt had the time to take the test.
MINOR DEFICIENCIES
1B. | Well #1,2,3 do not have flow meters prior to treatment. | Well #1,2,3 are required to have a means of measuring flow. | Minor Deficiencies | At time of review flow meter was not in working order and had not been for sometime. | Mort's water company will be installing new flow meters on wells #1,2,3 | 2015-04-30 | Nick Wilson |  |  | 2015-03-19 | Mort's have installed a water meters along with control boxes to measure waterflow.
1C. | Well #1,2,3 are not being tested for static and pumping water levels. | Static pressure and pumping water levels must recorded once a month. | Minor Deficiencies | Static pressure and water level recording had ceased due to Management and Personal changes. | Mort's water company will be Measuring static and water levels monthly. | 2015-02-27 | Nick Wilson |  |  |  | Mort's has not been out to due static pressure due to bio-secrtiy issues's
1F. | Well #3 is 57 feet from a farm field not owned by Sparboe farms Goodell and 2 feet away from a farm field owned by Saprobe farms Goodell. Well #2 is 80 feet away from a field owned by Sparboe farms Goodell. | legal control around wells did not meet requirements of the DNR. | Minor Deficiencies | Before the day of audit it was not known that wells legally required a 200-ft legal control around the Wells. | A verbal agreement with farmers will be established | 2015-03-13 | Nick Wilson |  |  | 2015-04-05 | Have back heard back only from one farmers
3B. | Barn three north has a bulk loading site with no backflow prevention. | This system must provide an positive separation from the potable water supply. | Minor Deficiencies | Upon review of audit, we had found an old load site. | Mort's water company will be removing old bulk load out site and capping this pipe. | 2015-03-13 | Nick Wilson |  |  | 2015-03-20 | We caped off the bulk loading.
3C. | A minimum free chlorine residual must be continuously maintained throughout the system except for those points which terminate in dead ends or very low areas. | Chlorine residuals should be continuously maintained. | Minor Deficiencies | Chlorine pumps and test kits were currently none operational and had not been functioning for some time. | Chlorine pumps have been ordered and chlorine tests have been ordered. | 2015-03-19 | Nick Wilson |  |  | 2015-04-20 | chlorine pump has been installed
6A. | The system is reminded all bacteriological analyses records, all monthly records for operation, all copies of reports, retained for a period of not less than 10 years. | During audit several records were missing and had not been retained during the last 4 years. | Minor Deficiencies | Records had not been retained with new Management and personal changes during the last 4 years | Records have been filed accordingly and future records will be organized and kept by Sparboe Goodell admins. | Effective Immediately 2/16/15 | Nick Wilson |  |  | 2015-02-16 | We organized records that were on site and filed them accordingly.
6B. | The system is reminded all records o f chemical analyses, all sanitary surveys and copies of all reports, summaries or communication related to sanitary surveys shall be retained for a period not less then 10 years. | Audit findings reviewed that records of chemical analyses, all sanitary surveys and copies of reports, summaries or communication related to sanitary surveys had not been retained for a period of time. | Minor Deficiencies | Records had not been retained with new Management and personal changes during the last 4 years | Records have been filed accordingly and future records will be organized and kept by Sparboe Goodell admins. | Effective Immediately 2/16/15 | Nick Wilson |  |  | 2015-02-16 | We organized records that were on site and filed them accordingly.
6C. | The system is reminded that all copies of reports, summaries or communication related to copies of public notices issued, and all records of actions taken to correct violations must be retained for a period not less than 3 years. | Audit findings revealed that records of public notices issued and all records of actions taken to correct violations and communication had not been retained for a period of time. | Minor Deficiencies | Records had not been retained with new Management and personal changes during the last 4 years | Records have been filed accordingly and future records will be organized and kept by Sparboe Goodell admins. | Effective Immediately 2/16/15 | Nick Wilson |  |  | 2015-02-16 | We organized records that were on site and filed them accordingly.
Summary of Requirements
1G. | There were some loose bolts on wells #2 and #3 they should be tightened | while inspecting the wells it was noticed that there was loose bolts on the well caps. | Requirement | Bolts were not tighten when last maintained | Replaced loose bolts with new nuts and bolts. | 2015-02-16 | Nick Wilson |  |  | 2015-02-16 | We have replaced some old bolts with new ones and have tighten up others.
2B. | Liquid chlorine pump has been broken since at least August 2014. | Chlorine treatment is required per our permit at all times. | Requirement | Chlorine pumps were not properly maintained. | Chlorine pumps have been ordered and waiting on install. | 2015-03-19 | Nick Wilson |  |  | 2015-04-20 | chlorine pump has been installed
2I. | It is unknown where the iron filtration backwash is discharged. It may be discharged to the industrial waste storage tank, septic tank, or to the farm tile. | During the audit we found that we can not locate were the discharge water from the iron filters flows. | Requirement | when facility was built there is no history on were water is discharged. | Mort's water company will be investigating into were discharge water is being discharged and make corrections to be compliant. | 2015-04-30 | Nick Wilson | 2015-05-30 |  |  | Mort's water company has decited not to proceed with investigating discharge. I am reaching out to yagy collbe to help with this.
2J. | A review of the Monthly Operation Report for sparboe Farms Goodell revealed the reports were not submitted for the past six months. | During the sanitary survey, we had all of the MORs for past year and gave a copy to Ashely Waller. | Requirement | New management and personal changes had caused MORs not be sent in on a timely manner. | Chlorine pumps have been ordered and chlorine tests have been ordered along with flow meters to ensure that MORs can accurately be filled out correctly. MORs will be tracked and logged on our Sparboe SharePoint system to ensure delivery to the DNR in a timely manner. | 2015-03-19 | Nick Wilson |  |  | 2015-04-02 | MOR's have been mailed for month of feburary.Mor's have been mailed for the month of March.
4A. | The floor of the chorine/pressure tank room is covered in approximately one inch of water with a dead mouse floating in it. This room should be drained of water and cleaned. The integrity of the leaking storage facility should be inspected to determine where the water is coming from. It is undetermined at this time if the leaking is coming from the pressure tanks or if it is coming from somewhere else. | During the audit we had found water coming from a location in the floor. | Requirement | Possible leak from an under ground source. | We have drained and dried most of the floor. Mort's water company will be digging around where the problem is located as soon as the frost dissipates. | 2015-04-10 | Nick Wilson |  |  | 2015-04-13 | Mort's has fixed the pipe that was leaking
Export Corrective Action Report to a New Excel Workbook to save and send to Facility