[image: image2.jpg]lowA DEPARTMENT OF NATURAL RESOURCES GOVERNOR KIM REYNOLDS
LT. GOVERNOR ADAM GREGG

DIRECTOR KAYLA LYON





February 26, 2021
SCOTT HUTCHENS






sthutchens@dmgov.org  
DM METRO WASTEWATER RECL. AUTHORITY
3000 VANDALIA RD

DES MOINES, IA 50317

SUBJECT: 
Permanent Closure of Underground Storage Tank Systems, piping only


DM Metro Wastewater Recl. Authority, 3000 Vandalia Rd, DM, IA


UST Registration No.  198602518

LUST No. 7LTJ03
Tentative Date of Closure 3/22/2021
Dear Mr. Hutchens:
The DNR UST Section has received the closure notification for the above-referenced location.  An Iowa licensed remover must be on site to supervise the permanent closure procedures.  It is essential that the licensed remover contact local authorities to obtain the necessary permits and to learn of specific requirements.

In accordance with Rule 567--135.15(455B) of the Iowa Administrative Code (IAC), certain procedures must be followed when an underground storage tank system is permanently closed.  Follow the steps outlined below that are further explained in the guidance document, which is posted on the UST Section website: http://www.iowadnr.gov/land/ust/ustremovers.html .

1. Always practice extreme care and safety during removal and disposal off-site or during tank fill-in-place procedures.  Workers will be exposed to hazardous, flammable and combustible liquids and vapors in the work area.  Benzene and tetraethyl lead are known cancer-causing agents.  Although lead has not been used in gasoline since the mid-1980s, lead residues may still be present in older tanks and in the soil around the tanks.  Use the DNR’s UST Permanent Closure Guidance documents and the following standards and practices when permanently closing underground storage tank systems:

· API RP 1604, “Removal and Disposal of Used Underground Petroleum Storage Tanks,” 

· API Publication 2015, “Cleaning Petroleum Storage Tanks”;

· API RP 1631, “Interior Lining of Underground Storage Tanks,”

· The National Institute for Occupational Safety and Health (NIOSH) “Criteria for a Recommended Standard…Working In Confined Space” may be used as guidance for conducting safe closure procedures at some hazardous substance tanks.
· NFPA 326: Standard for the Safeguarding of Tanks and Containers for Entry, Cleaning, or Repair

· NFPA 30: Flammable and Combustible Liquids Code, 30-93.

2. Drain any remaining product in the piping into the tank.  Vacuum and flush pipe with one or two gallons of water or nitrogen (more expensive, but generates less waste that has to be removed from the tank).  Disconnect piping from the tank.  Remove product piping.

3. Remove all liquids from the tank.  Use explosion-proof or air-operated pumps.  Vacuum trucks should be located upwind of the tank.  The suction hose must be grounded.  The exhaust gases must be vented at least 12 feet above ground surface.

4. Remove tank appurtenances (gauge pipes, fill pipes, STPs, etc.)  Leave vent line connected until the tank is purged or inerted.

5. Air purge the tank (force explosive vapors out) or inert the tank (remove or displace the oxygen in the tank).  When purging, a combustible gas meter is used to measure the reduction in the concentration of flammable vapors.  The meter reads from 0 to 100 percent of the LFL or LEL.  The goal is to achieve a reading below 10 percent LEL (NFPA 30, 2003 C.4.10).

6. API recommends inerting the tank with 1½ to 2 pounds of dry ice per 100 gallons of tank capacity.  Vapors must be vented at least 12 feet above ground.  Nitrogen gas may also be used to inert the tank.  The gas can be pumped into the tank from a hose through the fill hole to the bottom of the tank.

7. When inerting, use an oxygen meter to determine the oxygen concentration.  The meter reads 0-100 percent oxygen content.  The tank is safe for removal when a reading from 1-10 percent is achieved [NFPA 30, 2003, C.4.10 (2)].

8. Plug the openings, except for one 3 mm (1/8-inch) hole at the top of the tank, and remove the tank from the excavation.  Place it on a level surface and block it.

9. Vacuum flush or triple wash and rinse the tanks.  Remove all rinseate and sludge from tanks.  Tanks may be cleaned on site as long as it is approved by local public safety officials.  Tank cleaning must always be done at a safe location where public access can be restricted and where public safety is not compromised, and not on a sensitive geologic area.  Tank cleaning in busy urban areas is dangerous; the public must never be put at risk.

10. A certified groundwater professional must supervise the closure assessment.  Soil and groundwater samples must be collected and sent to an Iowa certified lab to be analyzed.    Contact the certified lab that will perform the analysis well before the closure takes place so all the materials are ready and available on the day of removal.  The number of samples to be collected is determined by the number and size of the tanks and length of piping (see guidance document on the DNR UST Section Website: http://www.iowadnr.gov/land/ust/ustremovers.html .

If you are installing a new UST system, please note: as of November 28, 2007, all UST systems must have secondary containment, i.e., double-wall tanks and piping, liquid-tight sumps and under dispenser containment.  When replacing piping within 10 feet of a dispenser or when piping is replaced below the check valve or shear valve, secondary containment requirements go into effect.

NOTE: If planning to install tanks or piping, an Intent to Install Notice needs sent to the DNR 30 days prior to install date. Please direct questions on installs to James.Gastineau@dnr.iowa.gov or by phone at 515.725.8450.

Contact the DNR Field Office in your region at least 24 hours before the actual closure to inform them of the time of removal (see Guidance Document for your region’s field office and phone number).

A closure report must be submitted to the department within 45 days of permanent closure.  Your registration record will be updated upon receipt of the closure report confirming the permanent closure of the tank system.  If you have any questions, contact me at 515.725.8336 or lisa.niedermayer@dnr.iowa.gov .

Sincerely,

[image: image1.png]



Lisa Niedermayer

Environmental Specialist

Underground Storage Tank Section

CC:
DNR FO 5, Ted Petersen, Bill Gross, emailed ted.petersen@dnr.iowa.gov, bill gross@dnr.iowa.gov 
John TeKippe, Fire Chief, Des Moines Fire Department, emailed jftekippe@dmgov.org 
Steve Ellsbury, Remover, Unified Contracting Services, Des Moines, IA, emailed stevellsbury@aol.com 
Brian Wiegert, PMMIC, Urbandale, emailed bjw@pmmic.com
James Gastineau, DNR Central Office, james.gastineau@dnr.iowa.gov 

WALLACE BUILDING, 502 E 9TH ST, DES MOINES IA 50319

Phone: 515-725-8200
www.IowaDNR.gov 
Fax: 515-725-8202

[image: image2.jpg]